## Slide 1
SUBSTATION FUNDAMENTALS
Substation Fundamentals, Finn 2020
SUBSTATIONS
PART 6 Secondary Systems
Module 2
Notes: * Edit the middle of the slide text to add the name of the tutorial organizer as appropriate.
** Edit the middle of the slide text to add the logo of the tutorial organizer as appropriate.
*** Edit the bottom of the slide text to add the presenter, location and date of the presentation.

## Slide 2: Part 6 – Secondary Systems
Notes: Presentation Timing: Total of ?? minutes at an average to fast pace without questions
Slides 0 to ?? covering Introduction = ?? min.
Slides ?? to ?? covering Definitions = ?? min.
Slides ?? to ?? covering Configurations = ?? min.
Slides ?? to ?? covering Design Process = ?? min.

## Slide 3
Module 1
Introduction
Auxiliary Systems
Protection
Metering and Monitoring
Part 6 – Outline

## Slide 4
Module 2
Manual and Automatic Control
Communications
Digital Equipment
Physical Security
Cyber Security
Part 6 – Outline

## Slide 5: Manual and Automatic Control
Manual Control
Basic Control Requirements
A control system is required for the substation in order to:-
Indicate the status of all plant in the substation.
Indicate all alarms for primary and secondary equipment.
Show analogue measurement for the key parameters V, A, W and Vars.
Provide digital outputs to close/open switchgear, raise/lower taps etc.
The control system may also control voltage, reactive power and load as well as employing interlocking and synchronizing.
The substation control will normally be effected from three locations although usually only one location will be operative at any one time.
In the switchyard/switchgear buildings (bay control).
At the substation control room (station control).
From a central network control centre (network control, remote control centre, regional control centre).
Notes: No specific notes.

## Slide 6: Manual and Automatic Control
Manual Control
Basic Control Requirements
An example of Human Machine Interface Locations
Notes: This example precedes modern computer control systems,

## Slide 7: Manual and Automatic Control
Manual Control
Interlocking
  Interlocking is applied by many utilities to ensure that all disconnectors, fixed earthing switches and where required circuit breakers are operated in the correct sequence so that operators do not compromise the integrity of the transmission system by incorrect or inadvertent operation of equipment or jeopardise the safety of personnel.
  The most common conditions covered by interlocking schemes are:-
Interlocking between disconnectors and circuit breakers to ensure that disconnectors do not make or break load currents.
Interlocking between disconnectors and earth switches to ensure that earth switches cannot be closed onto locally energized circuits and conversely earth switches cannot be energized when closed by closing of a disconnector.
Interlocking between disconnectors and adjacent earth switches to enable the disconnector to be operated for maintenance purposes when the earth switches either side are closed.
Notes: No specific notes.

## Slide 8: Manual and Automatic Control
Manual Control
Interlocking
The most common conditions covered by interlocking schemes (cont):-
To ensure correct sequence of on load transfer switching operations at multiple busbar substations and that a parallel path exists between the disconnectors connected to each bar. Some utilities block the tripping of a bus coupler or bus section which is providing the parallel path during bus transfer operation.
To ensure that a bus coupler or bus section circuit breaker can only be closed when the disconnectors either side are both closed (operational condition) or both open (maintenance condition).
To restrict access to areas of a substation where safety clearances may be infringed (e.g. filter equipment) unless appropriate safety measures have been taken such as isolation and earthing.
Where practicable interlocking schemes should allow the maximum operational flexibility, not unnecessarily impose fixed operating sequences, be inherently fail safe and it should not be possible to defeat them except with the use of tools or by a purpose designed lockable override facility.
Notes: No specific notes.

## Slide 9: Manual and Automatic Control
Manual Control
Interlocking
Electrical interlocking is usually used when the switching sequences involve only power operated switchgear. Ideally the correct interlocking status should be confirmed automatically on initiation of any operation whether by an operator or as part of an automatic sequence.
Mechanical interlocking is usually by means of key operated systems. The keys should be of a non masterable design (i.e. there should not be any possibility of a master key).
On more complicated interlocking schemes it may be necessary to provide key exchange boxes and these should be located at convenient points for the normal operation of the substation.
Occasionally electro mechanical key exchange boxes may be needed to link up the electrical and mechanical interlocking.
Notes: No specific notes.

## Slide 10: Manual and Automatic Control
Manual Control
Interlocking
  Traditionally electrical interlocking has been done by using hardwired contact logic.
  With computerised control systems the status of all of the plant is already known within the control system and so it is possible to write some software logic to perform the interlocking function.
  This significantly reduces the amount of cabling required on the site and it is very effective when applied to new Greenfield site substations.
  Problems can be encountered when additions or modifications are required at the substation. Usually this will involve building a mimic of the entire revised substation in the factory to test the modified interlock software before loading it onto the actual computer system on site.
Notes: The concerns with modifying software interlocking is that when making the required changes other items in the software are inadvertently changed.

## Slide 11: Manual and Automatic Control
Manual Control
Synchronising
Synchronising is required on transmission networks to:-
Ensure retention of system stability
Minimize damage to plant
Facilitate the re-paralleling of a split system
If circuit breakers are closed when the systems either side are not in synchronism then a shock load can be imposed on generators and a large flow of synchronising power will flow on the network.
On the transmission network two types of synchronising are usually employed namely check synchronising and system synchronising.
Notes: No specific notes.

## Slide 12: Manual and Automatic Control
Manual Control
Synchronising
Check synchronising usually occurs when the circuit breaker being closed is within a solidly connected system as shown in Diagram a.
System synchronising occurs when the circuit breaker being closed is connecting two independent systems as shown in Diagram b.
Notes: With check synchronizing there will be no slip between the voltages either side of the CB.

## Slide 13: Manual and Automatic Control
Manual Control
Synchronising
The conditions required for a synchronised close are:-
Same frequency on both sides of the CB (zero slip)
Zero phase angle difference between the voltages on both sides of the CB
Same voltage magnitude of approximately nominal value on both sides of the CB
The synchronising relay will check that these conditions are met within a certain tolerance.
Notes: No specific notes.

## Slide 14: Manual and Automatic Control
Manual Control
Conventional Human Machine Interface (HMI)
  HMI at bay level will comprise: control switches, indicator lamps and meters mounted on the equipment or in adjacent local control cubicles.
  Generally these facilities are used during maintenance of the controlled plant, or as back-up for use in the event of failure of the station level or central network control centre.
  At the station level, control panels should be located in the main control room. The HMI equipment should be grouped on a per-circuit basis, and open and close switches should only control equipment on the same section of the substation as the control panel represents and will normally include:-
  A mimic diagram representing the substation layout, usually in single line diagram form. Usually discrepancy switches will be used for both indication and control.
  Alarm annunciation equipment mounted adjacent to the mimic diagram, or form an integral part of the control panel.
Notes: If a computer control system is being used then the Station control will be a work station.

## Slide 15: Manual and Automatic Control
Manual Control
Introduction to Computer Based Control Systems
  With the rapid development of digital devices most substations nowadays are using computer based control systems. With these systems the control panels with mimic diagrams and alarm annunciators are replaced by:-
Visual display unit (VDU)
Alphanumeric keyboard
Printer
Plotter
Trackball
Joystick
Special function panel
Mouse
The mimic diagram is likely to be displayed as pages on the VDU.
Notes: No specific notes.

## Slide 16: Manual and Automatic Control
Manual Control
Basic Functions
  All control systems will contain the following basic functions.
    Control outputs – To close/open the various items of equipment.
    Status inputs – To indicate if the equipment is closed or opened
    Alarm conditions – to indicate any alarm conditions on any item of primary or secondary equipment.
    Analogue values – To indicate the key parameters in the substation such as MW, MVAr, V, I
  Many of these are carried out at the bay level.
  Usually at the station level there will be a standby control point which will allow complete control of the substation locally.
  If, as is becoming the norm these days, the station is unmanned then control will normally be carried out from the remote control centre.
Notes: No specific notes.

## Slide 17: Manual and Automatic Control
Manual Control
Additional Functions
In addition to the basic functions the following extra functions may also be built into the control system:-
Software interlocking – as the control system already knows the status of all of the equipment then the interlocking can be done using software logic instead of hardwired contact logic.
Synchronising – as busbar voltage transformers are not usually used, the control system does the voltage selection and checking of synchronism using software.
Automatic Tap Change Control (ATCC) – the control system provides logic to maintain voltage at a defined level and also keep transformer taps on transformers operating in parallel in line with each other.
Automatic Reactive Switching (ARS) – some Utilities use automatic switching of shunt reactors and shunt capacitors to control steady state voltages. The logic for this can either be built into the control system or the control system can communicate the relevant plant status information with another Intelligent Electronic Device (IED) which controls the reactive devices.
Notes: No specific notes.

## Slide 18: Manual and Automatic Control
Manual Control
Typical Architecture
The computer control system will still have the three levels for control namely bay level, station level and control centre level. A typical architecture is shown in the diagram.
Many current control systems still have hard wiring at the bay level but gradually with the development of the process bus this will change to fully digital.
Notes: No specific notes.

## Slide 19: Manual and Automatic Control
Manual Control
Modifications
Substation secondary systems may be extended or modified for any of the following reasons:
additional primary bays are required.
the substation configuration is altered.
primary equipment is changed.
additional secondary equipment is installed (e.g. busbar protection or remote control).
In order to facilitate the extension of the control system in a substation, spare capacity should be incorporated in cable trenches ducts and tunnels and in the central control building at the initial design stage. Spare space for adding additional cards should be made in computer control systems.
Notes: No specific notes.

## Slide 20: Manual and Automatic Control
Manual Control
Point on Wave Control
It is well known that transient surges can occur when closing or opening circuit breakers. The nature of the surges being dependent upon the particular item of plant being switched. Some examples are:-
Surges when closing long lines or composite circuits (line/cable/transformer) due to reflected waves.
Surges when closing in capacitor banks.
Inrush when energising large power transformers.
Induced voltages due to current chopping when de-energising shunt reactors.
The magnitude of many of these surges is dependent upon the specific point on the sine wave of either the voltage or the current at which the switching action occurs. For transformer energisation it may also be useful to take into account remanent flux.
Notes: No specific notes.

## Slide 21: Manual and Automatic Control
Manual Control
Point on Wave Control
As an example if we consider energising a long line where voltage doubling occurs on reflection of the voltage wave, then energising at a voltage zero would obviously drastically reduce the transient. The voltage zero occurs at different times on each phase so a CB with single phase mechanisms is preferred. (See diagram to the right)
The CB must have repeatable characteristics and the accuracy is important. The second diagram shows that for a 50Hz system where each half cycle is 10ms then missing the ideal point by 1ms (18deg) will mean applying a voltage of 30% (sin 18deg) of the peak voltage of the sine wave.
A point on wave relay is used which monitors the key parameters affecting CB closing time (e.g. hydraulic pressure, close coil voltage and temperature) and adjusts the time at which the close signal is sent to the CB to hit the desired point on wave.
Notes: The voltage doubling effect is like a wave at sea hitting the sea wall and bouncing back over itself doubling the depth.

## Slide 22: Manual and Automatic Control
Manual Control
Point on Wave Control
However when calculating the time to send the signal, account must be taken of pre-arcing which occurs before the contacts physically touch.
So the closing signal has to be adjusted to be sent to have the voltage zero at the pre-arc distance.
Pre-arcing
contact touch
Notes: No specific notes.

## Slide 23: First set of Questions

## Slide 24: Manual and Automatic Control
Automatic Control
Use of Auto-Reclose
The most common form of automatic switching is auto-reclosing applied to overhead line circuits.
In the early days operators soon realised that when an overhead line tripped out of service in the majority of cases the fault was transient in nature and that if the circuit was reclosed then the circuit would return to service without any need for intervention.
With transient faults once the fault arc has been extinguished and a short time allowed for the ionised air to clear from the fault vicinity the insulation strength of the air is fully restored and satisfactory for service.
Originally the reclosing was done manually by the operators but faster automatic re-closing can assist in maintaining system stability or system integrity under some fault conditions.
Notes: No specific notes.

## Slide 25: Manual and Automatic Control
Automatic Control
Types of Auto-Reclose
There are various different types of auto-reclose as follows:-
Single pole – only the faulted phase is opened and then reclosed.
Three pole – all three poles open and reclose even for single phase faults.
High Speed – reclosure takes place in less than one second.
Delayed – reclosure is time delayed for a period usually 10-30 seconds.
Which type of auto-reclose is used depends upon a number of factors:-
If the CB is fitted with single phase or three phase mechanism.
If the network is weak with limited interconnections then three phase reclose could split the network. This leads to the use of high speed single phase auto-reclose on such networks.
If three phase high speed is used there is a large risk of instability if the fault is persistent and not transient. This leads to the use of three phase delayed auto-reclose on strong highly interconnected networks.
Notes: Three phase delayed auto-reclose is very good at maintaining system integrity in strong networks during storm conditions where one circuit of a double circuit will trip out and a few minutes later the other circuit trips but by that time the auto reclose has restored the first circuit.

## Slide 26: Manual and Automatic Control
Automatic Control
Operation of Auto-Reclose
On distribution level circuits multiple attempts to reclose the circuit are allowed.
On transmission circuits it is normal to only perform one auto-reclose.
If the auto-reclose is unsuccessful then the circuit will remain out of service.
If the reclosure is successful then the auto-reclose relay resets and is available to reclose again on a later fault.
Judging whether or not the reclosure was successful or not is usually done by seeing how long the circuit remains in service after being reclosed. This time is known as the reclaim time and is usually about two seconds.
The auto-reclose will be locked out if the CB is not in a suitable condition for closing. (low hydraulic pressure, low gas pressure etc.)
Notes: No specific notes.

## Slide 27: Manual and Automatic Control
Automatic Control
Auto-isolation within Auto-Reclose
X
X
OHL
X 113
X 420
X
X
SGT
X 120
X 103
Auto-reclosing in the event of a fault is specific to overhead line circuits, however, automatic switching of other circuits may be integrated into an auto-reclose sequence.
Consider a mesh corner with OHL and SGT connected.
For a fault on the supergrid transformer SGT all of the CBs X120, X420, X405 and T10 open.
Then disconnector X113 is automatically opened with a check that there is no neutral current in the transformer.
X 405
T10
Then CB X405 at remote end of line closes.
Then CB X120 check synch closes
Then CB X420 check synch closes
Notes: This kind of switching enables the maximum amount of healthy equipment to be restored to service quickly following a fault.

## Slide 28: Manual and Automatic Control
Automatic Control
Automatic Closing
This is the automatic closing of a circuit breaker when system conditions deem it is necessary.
A simple example is when a transformer is on hot standby (LV CB open but disconnector closed). Assume that there are three transformers connected to a busbar but if more than two are in service the fault level is exceeded, but two transformers are needed to meet the load demand. (refer to diagram). In this case transformers A and B are in service and transformer C is on hot standby.
If either of transformers A or B trip out then the autoclose scheme will close the LV circuit breaker on C to maintain two transformers in service.
More complicated schemes may consider the status of several circuits in order to decide to automatically close the designated circuit breaker, such as bus sections/couplers.
Notes: No specific notes.

## Slide 29: Manual and Automatic Control
Automatic Control
Operational Tripping
As systems become more complex it is becoming more necessary to put automatic schemes into service to avoid thermal overloading leading to cascade tripping or system instability due to excess load or infeed. In simple terms such schemes work as follows:-
If certain strategic circuits trip this may put constraints on the amount of generation which can be exported or load which can be delivered.
The conditions (usually outages) likely to lead to problems are identified in advance.
Usually it is thermal overloading which is the concern and so operation in several seconds or minutes will usually be adequate.
If system stability is the concern tripping in less than one second will be required.
When the defined conditions occur then a signal is sent to trip a large generator (maybe 500-1000MW) or remove a large load block.
As the tripping will have serious system and commercial consequences it is essential that it is very secure against maloperation.
Notes: No specific notes.

## Slide 30: Manual and Automatic Control
Automatic Control
Automatic Tap Change Control
Automatic tap change control is used to control the voltage on the low voltage side of transformers as follows ( see diagram):-
A relay detects the voltage on the LV side of the transformers.
If the voltage falls outside of a pre-set deadband it will cause a tapchange to operate after a short time delay to bring the voltage within the deadband.
The timing of the tapchange has to be coordinated with other voltage controls to avoid hunting.
Notes: No specific notes.

## Slide 31: Manual and Automatic Control
Automatic Control
Automatic Tap Change Control
The diagram to the right shows how the timing can be achieved.
The scheme may be adjusted to control the voltage at a remote busbar by the addition of line drop compensation to allow for the voltage drop in the line.
Usually the voltage set point can be adjusted and may have a couple of pre-set points. In this case load shedding can be achieved by changing the set point voltage to a lower value.

## Slide 32: Manual and Automatic Control
Automatic Control
Automatic Tap Change Control
In more complicated substations the ATCC equipment may need to be capable of controlling the voltages on a number of different busbars by controlling the tap-changers on a number of different transformers.
To do this the ATCC equipment must automatically detect the topology of the low voltage substation and recognize the busbar grouping for transformer tap change control.
The schemes used to gather information on the status of the circuit breakers and disconnectors associated with the transformers, bus couplers and bus section switches in the substation by hardwired contact information.
With the increasing use of computerised control systems the ATCC function can be integrated into the control system by the use of suitable software, significantly reducing the amount of cabling on the site.
The scheme will ensure that the taps on parallel transformers connected between a pair of busbars are the same or within one tap of each other to avoid the circulation of reactive power between the parallel transformers.
Notes: No specific notes.

## Slide 33: Manual and Automatic Control
Automatic Control
Automatic Reactive Control
Voltage is normally controlled on a transmission network by the dispatching of reactive power from generators connected to the network.
Injecting more reactive power increases the system voltage whilst reducing the injection or even absorbing reactive power reduces the voltage.
As networks become more complex additional reactive plant is installed at substations remote from major generation sources in order to control the voltage.
This reactive plant may be either of the dynamic type, such as static voltage compensators (SVC) or the static type such as shunt capacitors or shunt reactors.
When both dynamic and static devices are connected they should be coordinated such that the steady state voltage control is carried out by the static devices and the dynamic plant is kept in reserve to respond to incidents on the network such as tripping of circuits or load rejection.
Notes: Although a static voltage compensator has the word static in its title, it is actually a fast acting dynamic device.

## Slide 34: Manual and Automatic Control
Automatic Control
Automatic Reactive Control
Static devices may be controlled by an automatic reactive switching (ARS) scheme.
Normally this will be after correcting LV voltage with ATCC.
This monitors the voltage at the HV busbars in the substation and controls it within specified preset limits (deadbands). (refer to diagram).
If the voltage exceeds the upper limit then any shunt capacitors will be switched out or if none are in service then a shunt reactor will be switched in.
If the voltage falls below the lower limit then any shunt reactors will be switched out or if none are in service then a shunt capacitor will be switched in.
Notes: No specific notes.

## Slide 35: Manual and Automatic Control
Automatic Control
Automatic Reactive Control
Rapid changes in voltage are usually controlled by dynamic voltage control devices such as SVCs or Statcoms.
The SVC uses power electronic components and so is very fast and can contribute to maintaining voltage stability.
The SVC has a voltage setpoint and a settable slope. (see butterfly diagram)
For voltages above setpoint reactive power is absorbed.
For voltages below setpoint reactive power is injected.
The amount of reactive power depends upon the voltage difference and the slope.
The smaller the slope percentage the tighter the control of voltage.
Notes: No specific notes.

## Slide 36: Manual and Automatic Control
Automatic Control
Frequency Control
For the frequency to remain steady the generation and the load must balance exactly.
This is normally achieved by the governors on the generators.
If there is insufficient available generation then the frequency will start to fall.
Under frequency relays are used to detect this situation and initiate load shedding by tripping specific circuits.
These relays may have a number of different stages so the least important loads are shed first and the more essential loads are shed last.
To avoid actual shedding of load use of the set points on the ATCC equipment can reduce load by reducing voltage. This would normally have to be done manually.
Notes: No specific notes.

## Slide 37: Manual and Automatic Control
Automatic Control
Load Control
The load on the network varies considerably during the day.
It would be useful if the peak could be reduced by smoothing out the load profile.
A simple way to achieve this, used in the past, was to offer preferential tariffs for using power at off peak times. However in this case the control of the load is in the hands of the consumer.
A solution to this has come with the development of “smart” technology which allows signals to be sent via the power wires to consumers premises to disconnect loads within the premises.
The consumer will be offered a financial incentive to allow certain loads (usually the least essential loads) to be disconnected at any time by the Utility.
This method puts the control into the hands of the Utility.
Notes: The smart control of loads is likely to become more prevalent with the increase in wind and solar generation.

## Slide 38: Communications
Introduction
Communications have become a consolidated activity as utilities increasingly invest in their own dedicated telecommunications infrastructure.
Secure, reliable communications lie at the core of today’s power delivery systems.
Communications are required for protection, control, metering, energy management systems and wide area monitoring as well as voice communications.
Protection imposes the most stringent performance requirements requiring channel propagation times of the order of 5-10ms and the network availability and integrity requirements are well beyond those of a mainstream telecommunications service.
Energy Management systems and their SCADA need ever more bandwidth combined with high resilience and flexibility.
It is common practice for utilities to implement back up control centres geographically remote from the main control facility requiring the transfer of substation connections between control centres in the event of a major incident.
More wide area applications using time synchronized measurements are being applied increasing the reliance on the telecommunications system.
Notes: No specific notes.

## Slide 39: Communications
Introduction
As the advancement of digital communication technology is driven by the telecommunications industry electric utilities typically buy versions of telecommunications industry products modified, to have greater surge withstand capability, wide temperature variations, withstand abnormal vibrations and immunity to electromagnetic, electrostatic and radio interference.
Data rates have increased from 300bps with serial communications to 1000Mbps with Ethernet, and distances from about 1.2km with serial communications to in excess of 70km using optical cables.
There have been a variety of proprietary and open protocols developed leading to the development of the IEC 61850.
IEC 61850 is being extended to cover the communications outside of the substation to the control centre.
Notes: No specific notes.

## Slide 40: Communications
Communications within the Substation
The driving factor for the introduction of new technologies for the collection and transmission of data was the need for information in real time, to improve productivity and reduce operation costs.
This led to the introduction of remote terminal units (RTU)s and programmable logic controllers (PLC)s
RTUs and PLCs allow remote control centres to receive information via a communications link.
RTUs and PLCs use serial communications with various protocols such as Modbus, Profibus, DeviceNet, ASCII, and other proprietary protocols.
Notes: No specific notes.

## Slide 41: Communications
Substation Automation with Electromechanical or Static Relays
Where the substation is fitted with electromechanical or electronic relays an intermediate device such as an RTU or PLC has to be installed to collect the relevant information such as:-
Analog quantities – current, voltage, power, energy, frequency
Relay alarms
Breaker status
Disconnector and earth switch status
Transformer temperature
Transformer oil levels
On load tap changer position
Breaker commands open/close
Disconnector commands open/close
Tap change raise/lower etc.
All of this information is collected in an analogue format, via transducers and I/O cards contained in the RTU or PLC, and is then digitized for transmission to the remote control centre.
Notes: No specific notes.

## Slide 42: Communications
Substation Automation with Numerical Relays
Where the substation is fitted with numerical multifunction relays, also known as intelligent electronic devices (IED) which communicate either directly to a Master computer or to a RTU, PLC or Gateway (Data Concentrator) different options dependent upon the type of communications can be used such as RS 232 pure serial, RS 485 daisy chain or Ethernet.
The diagram to the right shows a RS232 connection.
Notes: No specific notes.

## Slide 43: Communications
Substation Automation with Numerical Relays
RS 485 Daisy Chain connection
Ethernet Connection
Notes: The left hand diagram is similar to the pure serial but uses a daisy chain arrangement to connect to the data concentrator. The ethernet system is basically similar to internet communications.

## Slide 44: Communications
Information to be communicated external to the Substation
The information which has to be communicated outside of the substation is basically:-
Voice.
Data.
Video.
Signals as an essential part of a differential protection.
Protection signalling e.g. distance protection signalling or direct transfer trip (intertripping).
These signals are all communicated via a communication system using one of the types of media described in the next slide after the break.
Utilities although they will have a public telephone will not rely purely on the public telephone system and will often have
An internal PAX telephone system.
A direct connection telephone to the Control centre.
Notes: No specific notes.

## Slide 45: Second set of Questions

## Slide 46: Communications
Available Media for Communication
There are basically five different media which have been used over the years for communications from substations namely:-
Pilots Wires – either metallic or with amplifiers included. (now less common).
Power line carrier communications (PLCC) – Using the power line as the communication media (see diagram).
Microwave – used where short line of sight communications are adequate.
Satellite communications are useful for very long distances over difficult terrain and provides very high bandwidth but can have longer delays and be affected by weather.
Fibre optic cable - now becoming the most common media embedded or wrapped around OHL earth wires. Multi-mode fibre used within the substation and for short distances and single mode for long distance communications.
Notes: In the past pilot wires and power line carrier communications were dominant but in recent years they have been replaced mainly by optic fibres.

## Slide 47: Communications
Multiplexing
Multiplexing is the sharing of a communication medium by combining signals at a common point. When a multiplexed signal is received it has to be de-multiplexed to separate out the signals. There are three basic methods of multiplexing:-
Frequency division multiplexing (FDM)
Used mainly with analogue signals. A special version known as Wave division multiplexing (WDM) is sometimes used with fibre optic cables.
Time division multiplexing (TDM)
This is most commonly used with digital communications systems for substations.
Coded division multiplexing (CDM)
Not usually used for protection and control purposes.
Notes: No specific notes.

## Slide 48: Communications
Digital Hierarchies
In order to bundle a larger number of channels within the available media further levels of multiplexing which are structured in digital hierarchies are required.
Originally Plesiochronous Digital Hierarchy (PDH) was used.
These systems use “almost synchronous” channels in multiples of 64kbps which is the digital equivalent of an analogue channel but PDH has a number of disadvantages:-
It is not possible to extract or insert individual channels without firstly de-multiplexing and then re-multiplexing.
It does not support network management and performance monitoring.
This has led to the development of synchronous digital hierarchy (SDH) in Europe and Synchronous Optical Network (SONET) in America.
Notes: No specific notes.

## Slide 49: Communications
Digital Hierarchies
SONET/SDH provides significant advantages over PDH as follows:-
Reduction in equipment requirements and an increase in network reliability.
Provision of overhead and payload bytes – overhead bytes permit management of the payload bytes on an individual basis and allow centralised fault sectionalization.
Definition of a synchronous multiplexing format for carrying lower level digital signals and a synchronous structure which simplifies the interface to digital switches and add-drop multiplexers.
Equivalence of SONET and SDH Hierarchies
Availability of a set of generic standards which enable products from different vendors to be connected.
Definition of a flexible architecture capable of accommodating future applications with a variety of transmission rates.
There are two main types of synchronous ring architecture
2 fibre UPSR for SONET and SNCP for SDH.
2/4 fibre BLSR for SONET and MS-SPRing for SDH.
Notes: No specific notes.

## Slide 50: Communications
Digital Hierarchies
Explanation of UPSR. Information entering the ring is bridged at the path circuit level and transmitted on both fibres in opposite directions .
Switching from one path to the other is based on the health of the path at the point where it exits the ring.
One direction is the primary signal path and the other direction is the protected path.
Notes: No specific notes.

## Slide 51: Communications
Digital Hierarchies
Normal Flow
Protected Flow
As switching is determined at the receive end only, the path in one direction may switch over to the protected path whilst the other direction remains on the normal path thus giving rise to unequal delays. This can lead to problems with some differential protections.
Notes: No specific notes.

## Slide 52: Communications
Digital Hierarchies
In a BLSR topology half of the bandwidth is reserved for protection.
Both transmit and receive paths take the same route in opposite directions
Both are switched together thus eliminating any differential delay, although protected path delays are likely to be longer.
In normal mode the route from A to B follows Service 1 S1 while the route from B to A follows S2.
When a fault occurs A to B will follow P1 and B to A will follow P2.
Notes: This method is much better for protection signals.

## Slide 53: Communications
Basic Requirements for Protection Communications
The following aspects of a communication system are important for protection.
Speed – the speed used for protection is usually 64kbps suitable for full duplex operation.
Propagation delay – this is the time for the signal to travel from one end to the other. Usually a delay time of 6ms or less is required. However it is important that the delay time is stable under normal operation. It will change if the path is re-routed due to failure.
Differential delay – this is the difference in the time from A-B compared to B-A. This is very important for differential protections where typically the maximum acceptable differential delay will be of the order of 400 micro seconds.
Dependability – this is that the protection will operate when it should do.
Security – this is that the protection will not operate when it should not.
See Table for typical figures.
Redundancy – inherently increases dependability but reduces security. It is normal to provide duplicate and separate routes for first and second main protections.
Notes: No specific notes.

## Slide 54: Digital Equipment
Introduction
The majority of protection devices supplied to substations today are digital or numeric devices. These have many advantages over the older relays as follows:-
They can perform many functions (including different types of protection) from one device.
Perform control functions.
Provide fault and event recording and condition monitoring.
Have self supervision to detect when faulty and so require less maintenance.
Require less and smaller devices.
.
Other significant differences are:-
Much of the electrical protection scheme logic resides within the relays so it is no longer possible to follow the entire logic of the protection scheme from the schematic diagrams, so the internal logic of the relay must also be understood to comprehend the full scheme.
Schematic diagrams basically show connections of inputs and outputs.
In many cases the internal logic can also be changed or designed to suit a particular application, which can lead to less wiring.
Notes: The disadvantage of the increased flexibility is the increased possibility to make errors when selecting the complex array of settings.

## Slide 55: Digital Equipment
Introduction
The advantages also bring a number of challenges or considerations for the protection system designer and testing personnel.
There are a large number of settings to be managed giving rise to a higher possibility of errors.
It is important to switch off or disable functions or settings which are not being used.
The changes in equipment have an impact upon staff, who need to keep their knowledge up to date with the fast moving technology whilst maintaining knowledge to service any existing legacy equipment.
Departments such as protection, control and telecommunications which previously operated largely independently of each other need to work closer together or merge since the equipment now involves all of these disciplines. With the complexity and rapid change of modern numeric devices, some utilities may outsource more work to suppliers/manufacturers.
Notes: Utilities are having to adapt their organizational structure to cater for the new generation of equipment.

## Slide 56: Digital Equipment
Digital Systems within Substations – IEC61850
Substation automation systems have been used since the 1980s but they used proprietary protocols which were incompatible between suppliers. So IEC61850 was developed to achieve the following:-
Lower installation and maintenance costs through devices that reduce manual configuration.
Reduction in engineering and commissioning with standardised object models and naming conventions for all devices.
Use of standardized configuration files.
Provide peer-to-peer messaging for direct exchange of data between devices and a high speed process bus that enables sharing of instrumentation signals between devices.
Use of readily available TCP/IP and Ethernet technology.
A complete set of services for reporting, data access, event logging, and control sufficient for most applications.
Interoperability between products from different suppliers.
Sampled Value standards enabling the share of digitized analogues and reduction of the number of CTs and VTs required.
Notes: Interoperability has long been a goal for Utilities who do not like to be tied down to a particular supplier.

## Slide 57: Digital Equipment
Digital Systems within Substations – IEC61850
There are three levels of control architecture in a substation:-
Station level – containing the common equipment for the whole substation.
Bay level – containing the equipment specific for a particular bay.
Process level – containing the primary equipment such as instrument transformers, circuit breakers, disconnectors etc.
Connections between levels were traditionally copper wiring, the application of substation communication buses has led to a reduction of cabling. IEC 61850 enables devices from different manufacturers to be connected to the same communication bus and share information in a truly interoperable way.
Notes: No specific notes.

## Slide 58: Digital Equipment
Digital Systems within Substations – IEC61850
Traditionally the connections between the primary equipment and the control system have been by hard wiring as shown on the left side of the diagram.
With IEC61850 current and voltage transformer signals can be digitised via merging units and communicated to the protection and control equipment via a process bus.
Tripping signals too can be issued via GOOSE (generic object oriented system events) messages.
Notes: No specific notes.

## Slide 59: Digital Equipment
Digital Systems within Substations – Life Span
Digital devices have a lifetime of 10-15 years due to obsolescence of components and difficulty of continuing support by manufacturers, compared to 40+ years with electromechanical equipment.
This means that during a typical substation lifetime of 40 years the digital equipment will need to be replaced at least once if not twice during the lifetime of the substation. Consequently ease of replacement has to be considered at the initial stage of introduction.
The use of IEC 61850 can assist with the upgrading of equipment - the reduction of copper connections and use of Ethernet type connections instead mean that new devices can be connected to the substation bus, configured and tested in the substation environment before replacing the older unit.
Notes: This shorter life of secondary equipment is still a major challenge for Utilities as it is very difficult to get the outages necessary for replacing the equipment.

## Slide 60: Digital Equipment
Software and Firmware
As it is the firmware and software in the device which defines the device, the management of these can present its own challenges as different versions may not be compatible with each other.
New versions of devices, which may include additional functions or modified setting ranges etc. can be released by manufacturers by modifying the firmware.
If not managed correctly, this can pose challenges to utilities and owners – they could end up with several versions of seemingly identical relays, but which may contain subtly different functions and setting ranges, resulting in logic or setting files that may not be compatible between devices.
A way that some utilities overcome this is to approve a certain firmware/software version and then specify only that particular firmware version for any supply until such time as another version is approved by them. In this way they can be sure of the functionality of the device and its compatibility with their network and any spares which they may hold.
If this is not done, then the owner must be sure of the functionality contained within the devices and the differences between different versions in order to minimise the risks of maloperation.
Notes: It is important that the Utilities have a clear method by which they control this issue.

## Slide 61: Physical Security
Site and Equipment Access Controls
Physical security is important to ensure safe and secure working conditions for on-site staff, to prevent access by unauthorized personnel and to prevent damage to equipment by intruders. This requires the following care for access control:-
To prevent unauthorized access the substation should be located in a secure building.
In the case of AIS where the primary plant is outdoors the site should be enclosed by walls or fencing sufficiently high to prevent intruder access.
Gates and doors should normally be equipped with robust locks and key access controlled as part of the utilities security/control procedures. Gates and doors should be constructed to prevent their easy removal or damage by vandalism.
Windows should not be provided in buildings that are adjacent to and overlook public areas but where this is the case steel shutters or burglar bars should be fitted.
Relay panels, kiosks and switchgear cubicles should be securely locked at all times except for maintenance work or inspections. Issuing of keys for access to such plant should be controlled under an appropriate “permit to work” procedure.
Notes: No specific notes.

## Slide 62: Physical Security
Alarm Systems
The alarm system should detect any abnormal conditions within the substation that constitute a danger to staff or equipment and alert staff both on site and remotely e.g. control centre. It should be capable of manual and automatic activation and include:
Smoke/gas detection.
Fire protection operated.
Plant failure.
Protections operated.
Staff assembly/attention required.
Intruder system activation.
The alarm initiated should be audible throughout the site and have visible annunciators indicating the alarm cause. Alarms should be grouped in a relatively small number of categories.
Notes: No specific notes.

## Slide 63: Physical Security
CCTV and Intruder Alarms
Intruder alarm systems may be used to counter unauthorised access, burglary, vandalism, etc. Such systems consist of activating devices provided on doors and windows augmented by motion detectors within the site. The system is usually connected to the alarm system and may additionally be connected to a local police or security authority.
Suitably located CCTV cameras may be used to support the intruder alarms.
However CCTV may be used for plant monitoring particularly for locations that are difficult to access due to remoteness.
CCTV cameras can monitor plant that is behaving abnormally enabling early identification and intervention, thus facilitating the prompt switching out of equipment at risk.
Notes: CCTV cameras can to some extent replace the visual inspections made by staff when the sites used to be manned.

## Slide 64: Cyber Security
Introduction
The introduction of digital devices into the control and protection of substations has greatly improved the flexibility and ease of operation. However this deployment of electronic devices renders substation secondary systems vulnerable to malicious interference or attack from two sources:
  Cyber induced attacks
  Intentional electromagnetic interference (IEMI).
An example of the first type occurred in December 2015 when the control system for part of the Ukrainian network (involving 3 Distribution Companies, 30 substations and 230,000 consumers) was hacked and this caused several hours of disruption to the network.
IEMI is less common but can cause disruption and damage to the electronic control and protection systems.
In this course only a brief indication of these issues is given.
Notes: No specific notes.

## Slide 65: Cyber Security
Types of Cyber Attack
Cyber attacks can be grouped into four categories:-
Gathering attacks involve skimming or tampering with substation automation data, eavesdropping (listening & recording communication between P&C IEDs and authorized users), and performing traffic analysis of repeated patterns of communication.
Imitation and modification attacks such as spoofing, cloning, and replay to impersonate legitimate access to substation IEDs, and between substation IEDs, to obtain authorized access.
Blocking attacks designed to deplete substation IED resources, network resources, or interfere with communications using tactics such as denial of service, jamming, and malware.
Privacy attacks designed to disclose sensitive information about legitimate P&C users or groups.
Attacks can occur independently or jointly resulting in loss of P&C data confidentiality, integrity and availability.
Notes: Cyber attacks can be initiated simply by malicious individuals but a more worrying development is the organized attacks by foreign government agencies of terrorists.

## Slide 66: Cyber Security
Typical Threats to Substation Systems
Threats can be introduced at every stage of the implementation of the P&C system and some examples are listed below:-
Vulnerabilities introduced during development – these are vulnerabilities injected by the manufacturer and typically are that there are ways that malicious code can be injected into the software.
Deployment and maintenance vulnerabilities – these are vulnerabilities often caused by software services that are not usually utilized and hence not checked for weaknesses.
Firewall configuration errors – it is important that the firewall is configured correctly so that the users have confidence in it. Site acceptance testing and maintenance should check that the firewall configuration is correct.
Notes: The emphasis here is that precautions need to be taken at every stage of the development and use of the systems.

## Slide 67: Cyber Security
Typical Threats to Substation Systems
On-line password guessing – a back-off function should be employed limiting the number of incorrect guesses (typically set to three)
Off-line password guessing – sometimes it is possible for the attacker to retrieve system user credentials and then guess the password off-line.
Inadequate access controls – it is important that a user is given the correct level of privileges i.e. not too many so that they can alter things they should not be able to and not too few which may result in personnel sharing credentials.
Network traffic analysis and manipulation – if an attacker is able to listen to and record data in transit this can enable them to make various different attacks for example the attacker could replay previously sent messages and thus fool the system operators regarding the state of the power system or may be able to intercept passwords transmitted in clear text.
Notes: It is becoming more and more important that Utilities have defined and clear systems to protect against cyber attacks.

## Slide 68: Cyber Security
Practical Solutions
A prerequisite to successful cyber defence is:
Clear unambiguous utility security policies and procedures implemented throughout the organization. Measures may be mandated by government/regulatory agencies depending on the country.
Robust and reliable security mechanisms provided in the substation devices and services.
The network security will normally fulfil the following security functions:-
Access Control - strong identity mechanisms for all elements of a protection and control system connected to a network: users, devices, and applications.
Data confidentiality and integrity - encryption is optional, except where requirements and regulations mandate data confidentiality.
Threat detection and mitigation – The objective is to protect critical assets against cyber attacks and insider threats.
Device and platform integrity – Device protection against compromise must be resistant to cyber-induced attacks.
Notes: No specific notes.

## Slide 69: Cyber Security
Practical Solutions
The following points should be applied when implementing the cyber security system.
Ensure that cyber security is considered at factory acceptance tests.
Apply anti-virus software and ensure that up to date patches are installed for perimeter defence.
Use security scanners to obtain an objective assessment of the state of cybersecurity vulnerabilities.
Implement a strong whitelisting policy to protect access to the protection and control network and components. (“Whitelisting” is the opposite of “blacklisting” in that it is an approved list/register of a particular privilege, service, mobility, access or recognition. Only those on the list will be recognised and accepted.)
Periodically review all wireless remote access to the protection and control system.
Apply role-based access control to protect access control and user control privileges and constantly review and update to ensure it is satisfactory.
Ensure that security incidents are immediately reported to IT and security authorities via a pre-planned process.
Notes: No specific notes.

## Slide 70: Cyber Security
Intentional Electromagnetic Interference
Intentional Electromagnetic Interference (IEMI) is the, “Intentional malicious generation of electromagnetic energy introducing noise or signals into electric and electronic systems, thus disrupting, confusing or damaging these systems for terrorist or criminal purposes.”
Although IEMI is relatively rare if it is considered a threat then an assessment should be made basically by asking the following questions.
What are the EM threat environments from possible EM weapons?
How close can the attacker get to the building (stand-off distances)?
What EM shielding does the building itself provide?
What interfering EM signal levels could then be induced on the internal cabling?
What EM disturbance levels are needed to cause adverse effects to the equipment?
What level of EM protection is required to prevent interference?
Notes: No specific notes.

## Slide 71: Cyber Security
Intentional Electromagnetic Interference
In order to mitigate the effects of IEMI and prevent damage to or interference with the electronic components the following may be considered
Increase the stand-off distance by using fences to keep possible perpetrators futher away.
Use electromagnetic alarms to monitor the environment.
Improve the effectiveness of the shielding provided by the building.
Reduce the coupling to the cables, or restrict the effects of the coupled signals, by better cable layout, the use of shielded cables or the application of ferrites.
Protect the equipment against surges by the application of surge protection devices.
Maximise the use of optical fibre cables.
Notes: The money to be spent on protection against IEMI needs to be decided based upon the level of threat.

## Slide 72: Final Questions